## Load Calc
Kelly Electric LLC, Dwelling Service Load Calculation
Job: Hartwell residence, 312 Sycamore Lane, Doylestown, PA 18901
Method: standard calculation, single family dwelling. Prepared by Brandon Kelly, License ME-118455
Conditioned area: 2,400 sq ft. Nominal voltage: 240V.
Load | Basis | Volt-Amps
General lighting and receptacles | 2,400 sq ft at 3 VA | 7200
Small appliance circuits | 2 circuits at 1,500 VA | 3000
Laundry circuit | 1 circuit at 1,500 VA | 1500
Subtotal, general loads |  | 11700
Demand: first 3,000 VA at 100% |  | 3000
Demand: remaining 8,700 VA at 35% |  | 3045
Net general load after demand |  | 6045
Electric range | 8 kW unit, table demand | 8000
Clothes dryer | nameplate | 5000
Water heater | nameplate | 4500
Dishwasher | nameplate | 1200
Disposal | nameplate | 900
Heating and air handler | 24 A at 240V | 5760
EV charger circuit | 32 A at 240V | 7680
Total calculated load |  | 39085
Calculated demand current | 39,085 VA divided by 240V | 162.9
Recommended service size | next standard size above calculated demand, with spare capacity | 200 A
Note: calculated demand is about 163 A. A 200 A service is specified to carry the new EV charger circuit and leave headroom.