## Work Orders
WO Number | Date | Customer | Location | System Type | Issue | Resolution | Tech | Hours
WO-2026-0014 | 01/06/2026 | Suburban Square Mall | Naperville | Carrier 50XC RTU | Noisy operation, belt squeal | Replaced drive belt and tensioner | D. Perry | 4.5
WO-2026-0019 | 01/08/2026 | Mario's Ristorante | Naperville | Walk-in Cooler | Temperature running high | Found low refrigerant, leak test, sealed joint | D. Perry | 6
WO-2026-0027 | 01/13/2026 | Oak Brook Office Center | Oak Brook | Trane RTU | Quarterly PM | Filters, belts, coil cleaning, controls check | D. Perry | 5
WO-2026-0031 | 01/15/2026 | Naperville Cold Storage | Naperville | Bohn Evaporator | Ice buildup on evap coils | Defrost timer malfunction, replaced timer motor | D. Perry | 7
WO-2026-0038 | 01/22/2026 | River North Bar and Grill | Aurora | Manitowoc Ice Machine | Low ice production | Descaled water system, replaced water valve | D. Perry | 3.5
WO-2026-0045 | 01/27/2026 | DuPage Medical Group | Naperville | York Chiller | Annual oil analysis | Pulled oil samples, replaced filter drier | D. Perry | 4
WO-2026-0052 | 02/03/2026 | Suburban Square Mall | Naperville | Carrier 50XC RTU | Follow-up on belt replacement | Running clean, no issues found | D. Perry | 2
WO-2026-0058 | 02/04/2026 | Mario's Ristorante | Naperville | Walk-in Cooler | Refrigerant follow-up | Added R-404A, charge holding, no leak | D. Perry | 3
WO-2026-0063 | 02/06/2026 | Naperville Cold Storage | Naperville | Copeland Scroll Compressor | Compressor failure, no cooling | Replaced scroll compressor, evacuated and charged | D. Perry | 10
WO-2026-0071 | 02/10/2026 | River North Bar and Grill | Aurora | Manitowoc Ice Machine | Descale and sanitize | Full cleaning cycle, water quality test | D. Perry | 3.5
WO-2026-0079 | 02/13/2026 | DuPage Medical Group | Naperville | York Chiller | Oil analysis follow-up | Results normal, filter change completed | D. Perry | 4
WO-2026-0084 | 02/19/2026 | Holiday Inn Express | Naperville | Hoshizaki KM-901 | No ice production | Control board failure, replaced board | D. Perry | 5.5
WO-2026-0091 | 02/20/2026 | Naperville Cold Storage | Naperville | Condenser Unit | Condenser fan not running | Fan motor seized, replaced motor and capacitor | D. Perry | 6